{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Main","Check"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Main","index":0,"n_rows":21,"n_cols":5,"rows_kept":21,"cut":false,"hidden":false,"merged":[]}
[null,"湿り空気状態値(SI版)"]
[null,"2020年8月31日作成"]
[null,"非営利活動法人(NPO) 設備システム研究会"]
[]
[null,"大気圧",101.325,"[kPa]","初期化"]
[null,"海抜高度",null,"[m]","消去"]
[null,"乾球温度",24,"[℃]","保存"]
[null,"湿球温度",null,"[℃]","消去"]
[null,"相対湿度",60,"[%]","保存"]
[null,"絶対湿度",null,"[kg/kg']","消去"]
[null,"比エンタルピ",null,"[kJ/kg]","消去"]
[null,"比容積",null,"[m3/kg']","消去"]
[null,"露点温度",null,"[℃]","消去"]
[null,"水蒸気圧計算方法","ウェクスラー・ハイランド",null,"初期化"]
[null,"飽和水蒸気圧",null,"[kPa]"]
[null,"水蒸気圧",null,"[kPa]"]
[]
[null,"(注)大気圧または海抜高度と、以下7個中2個 (絶対湿度と露点温度の組合せは除く) を入力し「計算」ボタンを押す。"]
[null,"(注)計算式はプログラムのソースを参照。"]
[null,"(注)エラー処理は最小限。"]
[null,"(注)計算誤差あり。"]

{"sheet":"Check","index":1,"n_rows":23,"n_cols":15,"rows_kept":23,"cut":false,"hidden":false,"merged":[]}
["大気圧","大気圧","海抜高度","海抜高度","大気圧","大気圧","乾球温度","飽和水蒸気圧 by ゴフ・グラッチ","飽和水蒸気圧 by ゴフ・グラッチ","乾球温度","飽和水蒸気圧 by ウェクスラー・ハイランド","飽和水蒸気圧 by ウェクスラー・ハイランド","乾球温度","飽和水蒸気圧 by テーテンス","飽和水蒸気圧 by テーテンス"]
["[kPa]","[mmHg]","[m]","[m]","[kPa]","[mmHg]","[℃]","[kPa]","[mmHg]","[℃]","[kPa]","[mmHg]","[℃]","[kPa]","[mmHg]"]
[101.325,760,0,0,101.325,760,0,0.61,4.5999999999999996,0,0.61099999999999999,4.5999999999999996,0,0.61099999999999999,4.5999999999999996]
[96.259,722,410,500,95.183000000000007,713.9,5,0.871,6.5,5,0.872,6.5,5,0.872,6.5]
[91.192999999999998,684,842,1000,89.412999999999997,670.6,10,1.226,9.1999999999999993,10,1.228,9.1999999999999993,10,1.228,9.1999999999999993]
[86.126000000000005,646,1299,1500,83.992000000000004,630,15,1.7030000000000001,12.8,15,1.7050000000000001,12.8,15,1.7050000000000001,12.8]
[81.06,608,1784,2000,78.900999999999996,591.79999999999995,20,2.3359999999999999,17.5,20,2.339,17.5,20,2.3380000000000001,17.5]
[75.994,570,2300,2500,74.117999999999995,555.9,25,3.165,23.7,25,3.169,23.8,25,3.1669999999999998,23.8]
[70.927999999999997,532,2852,3000,69.623999999999995,522.20000000000005,30,4.2409999999999997,31.8,30,4.2460000000000004,31.8,30,4.242,31.8]
[65.861000000000004,494,3444,3500,65.403999999999996,490.6,35,5.6210000000000004,42.2,35,5.6280000000000001,42.2,35,5.6210000000000004,42.2]
[60.795000000000002,456,4084,4000,61.439,460.8,40,7.3739999999999997,55.3,40,7.383,55.4,40,7.3730000000000002,55.3]
[55.728999999999999,418,4780,4500,57.713999999999999,432.9,45,9.5809999999999995,71.900000000000006,45,9.593,72,45,9.5790000000000006,71.900000000000006]
[50.662999999999997,380,5542,5000,54.216000000000001,406.7,50,12.333,92.5,50,12.35,92.6,50,12.333,92.5]
[45.595999999999997,342,6384,5500,50.929000000000002,382,55,15.739000000000001,118,55,15.76,118.2,55,15.741,118.1]
[40.53,304,7326,6000,47.841999999999999,358.8,60,19.917000000000002,149.4,60,19.943999999999999,149.6,60,19.925999999999998,149.5]
[35.463999999999999,266,8394,6500,44.942,337.1,65,25.004999999999999,187.6,65,25.039000000000001,187.8,65,25.029,187.7]
[30.398,228,9626,7000,42.216999999999999,316.7,70,31.155000000000001,233.7,70,31.198,234,70,31.204999999999998,234.1]
[25.331,190,11084,7500,39.658000000000001,297.5,75,38.54,289.10000000000002,75,38.591999999999999,289.5,75,38.631999999999998,289.8]
[20.265000000000001,152,12868,8000,37.253999999999998,279.39999999999998,80,47.347000000000001,355.1,80,47.411999999999999,355.6,80,47.506999999999998,356.3]
[15.199,114,15168,8500,34.994999999999997,262.5,85,57.786999999999999,433.4,85,57.865000000000002,434,85,58.045999999999999,435.4]
[10.132999999999999,76,18410,9000,32.874000000000002,246.6,90,70.085999999999999,525.70000000000005,90,70.180000000000007,526.4,90,70.489999999999995,528.70000000000005]
[5.0659999999999998,38,23952,9500,30.881,231.6,95,84.497,633.79999999999995,95,84.608000000000004,634.6,95,85.102999999999994,638.29999999999995]
[0,0,282432,10000,29.009,217.6,100,101.288,759.7,100,101.419,760.7,100,102.17400000000001,766.4]