## Main
Wet Air Characteristic Value (SI version)
Generated on 31 Aug 2020
Non profit organization (NPO) Society for the Study of Mechanical Service System
Atomosphere Pressure | 101.325 | [kPa] | Init
Sea Level Height |  | [m] | Erase
Dry-Bulb Temperature | 24 | [degC] | Keep
Wet-Bulb Temperature |  | [degC] | Erase
Relative Humidity | 60 | [%] | Keep
Absolute Humidity |  | [kg/kg'] | Erase
Specific Enthalpy |  | [kJ/kg] | Erase
Specific Volume |  | [m3/kg'] | Erase
Dew Point Temperature |  | [degC] | Erase
Water Vapor Pressure Calculation Method | Wexler-Hyland |  | Init
Saturated Water Vapor Pressure |  | [kPa]
Water Vapor Pressure |  | [kPa]
(Note 1) Input Atmospheric Pressure or Sea Level Height and 2 of following 7 (excluding Combination of Absolute Humidity and Dew Point Temperature) and press "Cal" button.
(Note 2) Refer to program source for calculation formula.
(Note 3) Error handling is minimal.
(Note 4) There is a calculation error.

## Check
Atomosphere Pressure | Atomosphere Pressure | Sea Level Height | Sea Level Height | Atomosphere Pressure | Atomosphere Pressure | Dry-Bulb Temperature | Saturated Water Vapor Pressure by Goff-Gratch | Saturated Water Vapor Pressure by Goff-Gratch | Dry-Bulb Temperature | Saturated Water Vapor Pressure by Wexler-Hyland | Saturated Water Vapor Pressure by Wexler-Hyland | Dry-Bulb Temperature | Saturated Water Vapor Pressure by Tetens | Saturated Water Vapor Pressure by Tetens
[kPa] | [mmHg] | [m] | [m] | [kPa] | [mmHg] | [degC] | [kPa] | [mmHg] | [degC] | [kPa] | [mmHg] | [degC] | [kPa] | [mmHg]
101.325 | 760 | 0 | 0 | 101.325 | 760 | 0 | 0.61 | 4.6 | 0 | 0.611 | 4.6 | 0 | 0.611 | 4.6
96.259 | 722 | 410 | 500 | 95.183 | 713.9 | 5 | 0.871 | 6.5 | 5 | 0.872 | 6.5 | 5 | 0.872 | 6.5
91.193 | 684 | 842 | 1000 | 89.413 | 670.6 | 10 | 1.226 | 9.2 | 10 | 1.228 | 9.2 | 10 | 1.228 | 9.2
86.126 | 646 | 1299 | 1500 | 83.992 | 630 | 15 | 1.703 | 12.8 | 15 | 1.705 | 12.8 | 15 | 1.705 | 12.8
81.06 | 608 | 1784 | 2000 | 78.901 | 591.8 | 20 | 2.336 | 17.5 | 20 | 2.339 | 17.5 | 20 | 2.338 | 17.5
75.994 | 570 | 2300 | 2500 | 74.118 | 555.9 | 25 | 3.165 | 23.7 | 25 | 3.169 | 23.8 | 25 | 3.167 | 23.8
70.928 | 532 | 2852 | 3000 | 69.624 | 522.2 | 30 | 4.241 | 31.8 | 30 | 4.246 | 31.8 | 30 | 4.242 | 31.8
65.861 | 494 | 3444 | 3500 | 65.404 | 490.6 | 35 | 5.621 | 42.2 | 35 | 5.628 | 42.2 | 35 | 5.621 | 42.2
60.795 | 456 | 4084 | 4000 | 61.439 | 460.8 | 40 | 7.374 | 55.3 | 40 | 7.383 | 55.4 | 40 | 7.373 | 55.3
55.729 | 418 | 4780 | 4500 | 57.714 | 432.9 | 45 | 9.581 | 71.9 | 45 | 9.593 | 72 | 45 | 9.579 | 71.9
50.663 | 380 | 5542 | 5000 | 54.216 | 406.7 | 50 | 12.333 | 92.5 | 50 | 12.35 | 92.6 | 50 | 12.333 | 92.5
45.596 | 342 | 6384 | 5500 | 50.929 | 382 | 55 | 15.739 | 118 | 55 | 15.76 | 118.2 | 55 | 15.741 | 118.1
40.53 | 304 | 7326 | 6000 | 47.842 | 358.8 | 60 | 19.917 | 149.4 | 60 | 19.944 | 149.6 | 60 | 19.926 | 149.5
35.464 | 266 | 8394 | 6500 | 44.942 | 337.1 | 65 | 25.005 | 187.6 | 65 | 25.039 | 187.8 | 65 | 25.029 | 187.7
30.398 | 228 | 9626 | 7000 | 42.217 | 316.7 | 70 | 31.155 | 233.7 | 70 | 31.198 | 234 | 70 | 31.205 | 234.1
25.331 | 190 | 11084 | 7500 | 39.658 | 297.5 | 75 | 38.54 | 289.1 | 75 | 38.592 | 289.5 | 75 | 38.632 | 289.8
20.265 | 152 | 12868 | 8000 | 37.254 | 279.4 | 80 | 47.347 | 355.1 | 80 | 47.412 | 355.6 | 80 | 47.507 | 356.3
15.199 | 114 | 15168 | 8500 | 34.995 | 262.5 | 85 | 57.787 | 433.4 | 85 | 57.865 | 434 | 85 | 58.046 | 435.4
10.133 | 76 | 18410 | 9000 | 32.874 | 246.6 | 90 | 70.086 | 525.7 | 90 | 70.18 | 526.4 | 90 | 70.49 | 528.7
5.066 | 38 | 23952 | 9500 | 30.881 | 231.6 | 95 | 84.497 | 633.8 | 95 | 84.608 | 634.6 | 95 | 85.103 | 638.3
0 | 0 | 282432 | 10000 | 29.009 | 217.6 | 100 | 101.288 | 759.7 | 100 | 101.419 | 760.7 | 100 | 102.174 | 766.4